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	BR 832 195
	PremiumLine self-draining body safety shower with eye shower, floor mounted

	B-SAFETY PremiumLine self-draining body safety shower with eye shower, floor mounted
- base plate with 4 mounting holes of stainless steel, polished, diameter 200 mm
- stand pipe 1 ¼” of stainless steel three-part, polished, total height 2330 mm
- ball valve 1” of stainless steel, inclusive self-draining to the upper edge of the ball valve near the bottom, water inlet 1” male, DIN-DVGW tested and certificated
- activation with plastic foot lever actuation for body shower, total width 240 mm
- activation with plastic handle for eye shower, total width 105 mm
- wall shower arm ¾“ of stainless steel, polished, projection 560 mm
- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure 
- high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining
- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre
- integrated PremiumLine safety eye shower with two spray heads 45°, mounting height 900 mm, orientation of eye shower freely selectable on site
- connection pipe of stainless steel for easy installation and alignment of the shower, polished, water inlet ¾” male
- ball valve ½” of stainless steel, with lever actuation, DIN-DVGW tested and certificated, including self-draining to the upper edge of the ball valve near the bottom
- operating lever of stainless steel, polished, with large arrow in application direction
- high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork
- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure
- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre
- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717
- according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019
- DIN-DVGW tested and certificated
Manufacturer: B-SAFETY or equal
Article-No.: BR 832 195

Technical Specifications
Minimum flow pressure: 1.5 bar
Operating pressure: 1.5 to 3 bar
Flow rate body shower: 50 l/min
Water inlet: 1” male
Dimensions (H x W x D): 2330 x 240 x 800 mm

Technical specifications eye shower:
Minimum flow pressure: 1,5 bar
Operating pressure: 1,5 to 5 bar
Flow rate: 14 l/min

Product overview
BR 832 195: flow rate 50 l/min (hazard class I according to EN 15154-5:2019)
BR 832 195 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)
BR 832 195 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019)
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Safety showers for hot climates

www.b-safety.com
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