| BR 861 095 | PremiumLine safety shower combination, with safety eye shower, wall mounted, exposed pipework |
| --- | --- |
| PremiumLine safety shower combination, with safety eye shower, wall mounted, exposed pipework - including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel - wall flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female - connection piece ¾” of stainless steel, for easy installation and alignment of the shower - ball valve ¾” of stainless steel, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, polished, length 700 mm - wall shower arm ¾“ of stainless steel, polished, projection 625 mm - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - two connection pipes ¾“ of stainless steel, polished, total length 1500 mm - wall flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female - integrated PremiumLine safety eye shower with two spray heads 45° - connection pipe of stainless steel for easy installation and alignment of the shower, polished, water inlet ¾” male - ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated - big push plate made of stainless steel, polished, length 130 mm, with large signal "PUSH", luminescent according to DIN 67510 - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely scale-free, with rubber sleeves and sealed dust caps - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre - mounting height 810 mm (± 100 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717 - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 861 095 Technical Specifications Minimum flow pressure: 1.5 bar Operating pressure: 1.5 to 3 bar Flow rate body shower: 50 l/min Water inlet: ¾“ female Dimensions: (H x W x D): 1625 x 230 x 625 mm Technical specifications eye shower Minimum flow pressure: 1,5 bar Operating pressure: 1,5 bis 5 bar Flow rate: 14 l/min Product overview BR 861 095: flow rate 50 l/min (hazard class I according to EN 15154-5:2019) BR 861 095 / 75L: flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019) BR 861 095 / 110L: flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |  |